Copyright 2017 by The American Institute of Architects (AIA)

Exclusively published and distributed by AVITRU, LLC for the AIA

This Product MasterSpec Section is licensed by AVITRU, LLC to Oatey ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Avitru or The American Institute of Architects (AIA). Neither AIA nor Avitru are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Oatey, 20600 Emerald Pkwy, Cleveland, OH 44135; Phone: (216) 267-7100; Website: www.oatey.com; Email: info@oatey.com.

For information about MasterSpec, contact Avitru at (800) 424-5080 or visit www.avitru.com.

SECTION 221119 - DOMESTIC WATER PIPING SPECIALTIES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Vacuum breakers.

          - Backflow preventers.

          - Water pressure-reducing valves.

          - Automatic water shutoff valves.

          - Balancing valves.

          - Temperature-actuated, water mixing valves.

          - Strainers.

          - Outlet boxes.

          - Hose stations.

          - Hose bibbs.

          - Wall hydrants.

          - Ground hydrants.

          - Post hydrants.

          - Drain valves.

          - Water-hammer arresters.

          - Air vents.

          - Trap-seal primer valves.

          - Trap-seal primer systems.

          - Flexible connectors.

          - Water meters.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 220519 "Meters and Gauges for Plumbing Piping" for thermometers, pressure gauges, and flow meters in domestic water piping.

          - Section 221116 "Domestic Water Piping" for water meters.

          - Section 223200 "Domestic Water Filtration Equipment" for water filters in domestic water piping.

          - Section 224300 "Medical Plumbing Fixtures" for thermostatic mixing valves for sitz baths, thermostatic mixing-valve assemblies for hydrotherapy equipment, and outlet boxes for dialysis equipment.

          - Section 224500 "Emergency Plumbing Fixtures" for water tempering equipment.

          - Section 224713 "Drinking Fountains" for water filters for water coolers.

          - Section 224716 "Pressure Water Coolers" for water filters for water coolers.

          - Section 224723 "Remote Water Coolers" for water filters for water coolers.

      - ACTION SUBMITTALS

For submittal documents for Oatey products, see www.oatey.com.

        - Product Data: For each type of product.

Retain "Shop Drawings" Paragraph below if retaining "Trap-Seal Primer Systems" Article.

        - Shop Drawings: For domestic water piping specialties.

          - Include diagrams for power, signal, and control wiring.

        - Sustainable Design Submittals:

"Product Data" Subparagraph below applies to LEED 2009, LEED v4, IgCC, and Green Globes for fixtures and equipment that consume water.

          - Product Data: For water consumption.

      - INFORMATIONAL SUBMITTALS

        - Field quality-control reports.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For domestic water piping specialties to include in emergency, operation, and maintenance manuals.

- PRODUCTS

Manufacturers and products listed in SpecAgent and MasterWorks Paragraph Builder are neither recommended nor endorsed by the AIA or Avitru. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - GENERAL REQUIREMENTS FOR PIPING SPECIALTIES

Retain both options in first paragraph below if plastic piping specialties are required.

        - Potable-water piping and components shall comply with NSF 61[ and NSF 14].[ Mark "NSF-pw" on plastic piping components.]

        - Comply with NSF 372 for low lead.

      - PERFORMANCE REQUIREMENTS

Coordinate this article with Section 221116 "Domestic Water Piping."

        - Minimum Working Pressure for Domestic Water Piping Specialties: [125 psig (860 kPa)] <Insert value> unless otherwise indicated.

      - VACUUM BREAKERS

Copy "Pipe-Applied, Atmospheric-Type Vacuum Breakers" Paragraph below and re-edit for each type of vacuum breaker required. If only one type is required, drawing designation may be omitted.

Pipe-applied, atmospheric-type vacuum breakers in first paragraph below are for moderate to high hazard and are available in NPS 1/4 to NPS 3 (DN 8 to DN 80). They are unsuitable for continuous pressure or for protection from backflow.

        - Pipe-Applied, Atmospheric-Type Vacuum Breakers <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Ames Fire & Waterworks; a WATTS brand.

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - Cash Acme, a Division of Reliance Worldwide Corporation.

            - FEBCO; a WATTS brand.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1001.

          - Size: NPS 1/4 to NPS 3 (DN 8 to DN 80), as required to match connected piping.

          - Body: Bronze.

          - Inlet and Outlet Connections: Threaded.

          - Finish: [Rough bronze] [Chrome plated].

Copy "Hose-Connection Vacuum Breakers" Paragraph below and re-edit for each type of vacuum breaker required. If only one type is required, drawing designation may be omitted.

Hose-connection vacuum breakers in first paragraph below are for low hazard and are unsuitable for continuous pressure. Outlet size is garden-hose thread.

        - Hose-Connection Vacuum Breakers <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - Arrowhead Brass Products.

            - Cash Acme, a Division of Reliance Worldwide Corporation.

            - Legend Valve & Fitting, Inc.

            - MIFAB, Inc.

            - Prier Products, Inc.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1011.

          - Body: Bronze, nonremovable, with manual drain.

          - Outlet Connection: Garden-hose threaded complying with ASME B1.20.7.

          - Finish: [Chrome or nickel plated] [Rough bronze].

Copy "Pressure Vacuum Breakers" Paragraph below and re-edit for each type of vacuum breaker required. If only one type is required, drawing designation may be omitted.

Pressure vacuum breakers in first paragraph below are for moderate to high hazard and are available in NPS 1/2 to NPS 2 (DN 15 to DN 50).

        - Pressure Vacuum Breakers <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Ames Fire & Waterworks; a WATTS brand.

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - FEBCO; a WATTS brand.

            - Flomatic Corporation.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1020.

          - Operation: Continuous-pressure applications.

          - Pressure Loss: [5 (35)] <Insert value> psig (kPa) maximum, through middle third of flow range.

          - Size: <Insert NPS (DN)>.

          - Design Flow Rate: <Insert gpm (L/s)>.

          - Selected Unit Flow Range Limits: <Insert gpm (L/s)>.

          - Pressure Loss at Design Flow Rate: <Insert psig (kPa)>.

          - Accessories:

            - Valves: Ball type, on inlet and outlet.

Copy "Laboratory-Faucet Vacuum Breakers" Paragraph below and re-edit for each type of vacuum breaker required. If only one type is required, drawing designation may be omitted.

Laboratory-faucet vacuum breakers in first paragraph below are for moderate to low hazard and are available in NPS 1/4 and NPS 3/8 (DN 8 and DN 10).

        - Laboratory-Faucet Vacuum Breakers <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by the following:

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1035.

          - Size: NPS 1/4 or NPS 3/8 (DN 8 or DN 10) matching faucet size.

          - Body: Bronze.

          - End Connections: Threaded.

          - Finish: Chrome plated.

Copy "Spill-Resistant Vacuum Breakers" Paragraph below and re-edit for each type of vacuum breaker required. If only one type is required, drawing designation may be omitted.

Spill-resistant vacuum breakers in paragraph below are for high hazard and are available in NPS 1/4 to NPS 1 (DN 8 to DN 25).

        - Spill-Resistant Vacuum Breakers <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by the following:

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1056.

          - Operation: Continuous-pressure applications.

          - Size: [NPS 1/4 (DN 8)] [NPS 3/8 (DN 10)] [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] [NPS 1 (DN 25)].

          - Accessories:

            - Valves: Ball type, on inlet and outlet.

      - BACKFLOW PREVENTERS

Copy "Intermediate Atmospheric-Vent Backflow Preventers" Paragraph below and re-edit for each type of backflow preventer required. If only one type is required, drawing designation may be omitted.

Intermediate atmospheric-vent backflow preventers in first paragraph below are for moderate hazard and are available in NPS 1/2 and NPS 3/4 (DN 15 and DN 20).

        - Intermediate Atmospheric-Vent Backflow Preventers <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - Cash Acme, a division of Reliance Worldwide Corporation.

            - FEBCO; a WATTS brand.

            - Honeywell.

            - Legend Valve & Fitting, Inc.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1012.

          - Operation: Continuous-pressure applications.

          - Size: [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)].

          - Body: Bronze.

          - End Connections: [Union, solder] [Solder] joint.

          - Finish: [Chrome plated] [Rough bronze].

Copy "Reduced-Pressure-Principle Backflow Preventers" Paragraph below and re-edit for each type of backflow preventer required. If only one type is required, drawing designation may be omitted.

Reduced-pressure-principle backflow preventers in first paragraph below are for high hazard and are available in NPS 3/4 to NPS 10 (DN 20 to DN 250).

        - Reduced-Pressure-Principle Backflow Preventers <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Ames Fire & Waterworks; a WATTS brand.

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - FEBCO; a WATTS brand.

            - Flomatic Corporation.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1013.

          - Operation: Continuous-pressure applications.

          - Pressure Loss: [12 psig (83 kPa)] <Insert value> maximum, through middle third of flow range.

          - Size: <Insert NPS (DN)>.

          - Design Flow Rate: <Insert gpm (L/s)>.

          - Selected Unit Flow Range Limits: <Insert gpm (L/s)>.

          - Pressure Loss at Design Flow Rate: <Insert psig (kPa)> for sizes NPS 2 (DN 50) and smaller; <Insert psig (kPa) value> for NPS 2-1/2 (DN 65) and larger.

          - Body: Bronze for NPS 2 (DN 50) and smaller; [cast iron with interior lining that complies with AWWA C550 or that is FDA approved] [steel with interior lining that complies with AWWA C550 or that is FDA approved] [stainless steel] for NPS 2-1/2 (DN 65) and larger.

          - End Connections: Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

          - Configuration: Designed for [horizontal, straight-through] [vertical-inlet, horizontal-center-section, and vertical-outlet] [vertical] <Insert configuration> flow.

          - Accessories:

            - Valves NPS 2 (DN 50) and Smaller: Ball type with threaded ends on inlet and outlet.

            - Valves NPS 2-1/2 (DN 65) and Larger: Outside-screw and yoke-gate type with flanged ends on inlet and outlet.

            - Air-Gap Fitting: ASME A112.1.2, matching backflow-preventer connection.

Copy "Double-Check, Backflow-Prevention Assemblies" Paragraph below and re-edit for each type of backflow-prevention assembly required. If only one type is required, drawing designation may be omitted.

Double-check, backflow-prevention assemblies in first paragraph below are for low hazard and are available in NPS 3/4 to NPS 10 (DN 20 to DN 250).

        - Double-Check, Backflow-Prevention Assemblies <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Ames Fire & Waterworks; a WATTS brand.

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - FEBCO; a WATTS brand.

            - Flomatic Corporation.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1015.

          - Operation: Continuous-pressure applications unless otherwise indicated.

          - Pressure Loss: [5 psig (35 kPa)] <Insert value> maximum, through middle third of flow range.

          - Size: <Insert NPS (DN)>.

          - Design Flow Rate: <Insert gpm (L/s)>.

          - Selected Unit Flow Range Limits: <Insert gpm (L/s)>.

          - Pressure Loss at Design Flow Rate: <Insert psig (kPa)> for sizes NPS 2 (DN 50) and smaller; <Insert psig (kPa)> for NPS 2-1/2 (DN 65) and larger.

          - Body: Bronze for NPS 2 (DN 50) and smaller; [cast iron with interior lining that complies with AWWA C550 or that is FDA approved] [steel with interior lining that complies with AWWA C550 or that is FDA approved] [stainless steel] for NPS 2-1/2 (DN 65) and larger.

          - End Connections: Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

          - Configuration: Designed for [horizontal, straight-through] <Insert configuration> flow.

          - Accessories:

            - Valves NPS 2 (DN 50) and Smaller: Ball type with threaded ends on inlet and outlet.

            - Valves NPS 2-1/2 (DN 65) and Larger: Outside-screw and yoke-gate type with flanged ends on inlet and outlet.

Copy "Beverage-Dispensing-Equipment Backflow Preventers" Paragraph below and re-edit for each type of backflow preventer required. If only one type is required, drawing designation may be omitted.

Beverage-dispensing-equipment backflow preventers in first paragraph below are for moderate hazard and are available in NPS 1/4 and NPS 3/8 (DN 8 and DN 10).

        - Beverage-Dispensing-Equipment Backflow Preventers <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by the following:

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1022.

          - Operation: Continuous-pressure applications.

          - Size: NPS 1/4 or NPS 3/8 (DN 8 or DN 10).

          - Body: Stainless steel.

          - End Connections: Threaded.

Copy "Dual-Check-Valve Backflow Preventers" Paragraph below and re-edit for each type of backflow preventer required. If only one type is required, drawing designation may be omitted.

Dual-check-valve backflow preventers in first paragraph below are for low hazard and are available in NPS 1/2 to NPS 1-1/4 (DN 15 to DN 32).

        - Dual-Check-Valve Backflow Preventers <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - A.Y. McDonald Mfg. Co.

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - Cash Acme, a division of Reliance Worldwide Corporation.

            - FEBCO; a WATTS brand.

            - Flomatic Corporation.

            - Ford Meter Box Company, Inc. (The).

            - Honeywell.

            - Legend Valve & Fitting, Inc.

            - Mueller Co.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1024.

          - Operation: Continuous-pressure applications.

          - Size: [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] [NPS 1-1/4 (DN 32)].

          - Body: Bronze with union inlet.

Copy "Carbonated-Beverage-Dispenser, Dual-Check-Valve Backflow Preventers" Paragraph below and re-edit for each type of backflow preventer required. If only one type is required, drawing designation may be omitted.

Carbonated-beverage-dispenser, dual-check-valve backflow preventers in first paragraph below are for moderate hazard and are available in NPS 1/4 and NPS 3/8 (DN 8 and DN 10).

        - Carbonated-Beverage-Dispenser, Dual-Check-Valve Backflow Preventers <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Cash Acme, a division of Reliance Worldwide Corporation.

            - Lancer Corporation.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1032.

          - Operation: Continuous-pressure applications.

          - Size: NPS 1/4 or NPS 3/8 (DN 8 or DN 10).

          - Body: Stainless steel.

          - End Connections: Threaded.

Copy "Reduced-Pressure-Detector, Fire-Protection, Backflow-Preventer Assemblies" Paragraph below and re-edit for each type of backflow-preventer assembly required. If only one type is required, drawing designation may be omitted.

Reduced-pressure-detector, fire-protection, backflow-preventer assemblies in first paragraph below are for high hazard and are available in NPS 3 to NPS 10 (DN 80 to DN 250).

        - Reduced-Pressure-Detector, Fire-Protection, Backflow-Preventer Assemblies <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Ames Fire & Waterworks; a WATTS brand.

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - FEBCO; a WATTS brand.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1047 and is FM Global approved or UL listed.

          - Operation: Continuous-pressure applications.

          - Pressure Loss: [12 psig (83 kPa)] <Insert value> maximum, through middle third of flow range.

          - Size: <Insert NPS (DN)>.

          - Design Flow Rate: <Insert gpm (L/s)>.

          - Selected Unit Flow Range Limits: <Insert gpm (L/s)>.

          - Pressure Loss at Design Flow Rate: <Insert psig (kPa)>.

          - Body: [Cast iron with interior lining that complies with AWWA C550 or that is FDA approved] [Steel with interior lining that complies with AWWA C550 or that is FDA approved] [Stainless steel].

          - End Connections: Flanged.

          - Configuration: Designed for [horizontal, straight-through] [vertical-inlet, horizontal-center-section, and vertical-outlet] [vertical] <Insert configuration> flow.

          - Accessories:

            - Valves: Outside-screw and yoke-gate type with flanged ends on inlet and outlet.

            - Air-Gap Fitting: ASME A112.1.2, matching backflow-preventer connection.

            - Bypass: With displacement-type water meter, shutoff valves, and reduced-pressure backflow preventer.

Copy "Double-Check, Detector-Assembly Backflow Preventers" Paragraph below and re-edit for each type of backflow preventer required. If only one type is required, drawing designation may be omitted.

Double-check, detector-assembly backflow preventers in first paragraph below are for low hazard and are available in NPS 3 to NPS 10 (DN 80 to DN 250).

        - Double-Check, Detector-Assembly Backflow Preventers <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Ames Fire & Waterworks; a WATTS brand.

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - FEBCO; a WATTS brand.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1048 and is FM Global approved or UL listed.

          - Operation: Continuous-pressure applications.

          - Pressure Loss: [5 psig (35 kPa)] <Insert value> maximum, through middle third of flow range.

          - Size: <Insert NPS (DN)>.

          - Design Flow Rate: <Insert gpm (L/s)>.

          - Selected Unit Flow Range Limits: <Insert gpm (L/s)>.

          - Pressure Loss at Design Flow Rate: <Insert psig (kPa)>.

          - Body: [Cast iron with interior lining that complies with AWWA C550 or that is FDA approved] [Steel with interior lining that complies with AWWA C550 or that is FDA approved] [Stainless steel].

          - End Connections: Flanged.

          - Configuration: Designed for [horizontal, straight-through] [vertical-inlet, horizontal-center-section, and vertical-outlet] [vertical] <Insert configuration> flow.

          - Accessories:

            - Valves: Outside-screw and yoke-gate type with flanged ends on inlet and outlet.

            - Bypass: With displacement-type water meter, shutoff valves, and reduced-pressure backflow preventer.

Copy "Hose-Connection Backflow Preventers" Paragraph below and re-edit for each type of backflow preventer required. If only one type is required, drawing designation may be omitted.

Hose-connection backflow preventers in first paragraph below are for high hazard. Outlet size is garden-hose thread. Caution: Availability is limited.

        - Hose-Connection Backflow Preventers <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by the following:

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1052.

          - Operation: Up to 10-foot head of water (30-kPa) back pressure.

          - Inlet Size: NPS 1/2 or NPS 3/4 (DN 15 or DN 20).

          - Outlet Size: Garden-hose thread complying with ASME B1.20.7.

          - Capacity: At least 3-gpm (0.19-L/s) flow.

Copy "Backflow-Preventer Test Kits" Paragraph below and re-edit for each type of test kit required. If only one type is required, drawing designation may be omitted.

Backflow-preventer test kits in paragraph below are suitable for pressure vacuum breakers; reduced-pressure-principle backflow preventers; double-check, backflow-prevention assemblies; and double-check, detector-assembly backflow preventers.

        - Backflow-Preventer Test Kits <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - FEBCO; a WATTS brand.

            - Flomatic Corporation.

            - <Insert manufacturer's name>.

          - Description: Factory calibrated, with gages, fittings, hoses, and carrying case with test-procedure instructions.

      - WATER PRESSURE-REDUCING VALVES

Copy "Water Regulators" Paragraph below and re-edit for each type of water regulator required. If only one type is required, drawing designation may be omitted.

Water regulators in first paragraph below are available in NPS 1/2 to NPS 3 (DN 15 to DN 80).

        - Water Regulators <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - Cash Acme, a division of Reliance Worldwide Corporation.

            - Honeywell.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1003.

          - Pressure Rating: Initial working pressure of 150 psig (1035 kPa).

          - Size: <Insert NPS (DN)>.

          - Design Flow Rate: <Insert gpm (L/s)>.

          - Design Inlet Pressure: <Insert psig (kPa)>.

          - Design Outlet Pressure Setting: <Insert psig (kPa)>.

          - Body: Bronze[ with chrome-plated finish] for NPS 2 (DN 50) and smaller; cast iron[ with interior lining that complies with AWWA C550 or that is FDA approved] for NPS 2-1/2 and NPS 3 (DN 65 and DN 80).

          - Valves for Booster Heater Water Supply: Include integral bypass.

          - End Connections: Threaded for NPS 2 (DN 50) and smaller; flanged for NPS 2-1/2 and NPS 3 (DN 65 and DN 80).

Copy "Water-Control Valves" Paragraph below and re-edit for each type of water-control valve required. If only one type is required, drawing designation may be omitted.

Water-control valves in paragraph below are available in NPS 1-1/4 (DN 32) and larger.

        - Water-Control Valves <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - American Standard.

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - CLA-VAL Automatic Control Valves.

            - Flomatic Corporation.

            - OCV Control Valves.

            - <Insert manufacturer's name>.

          - Description: Pilot-operated, diaphragm-type, single-seated, main water-control valve.

          - Pressure Rating: Initial working pressure of 150 psig (1035 kPa) minimum with AWWA C550 or FDA-approved, interior epoxy coating. Include small pilot-control valve, restrictor device, specialty fittings, and sensor piping.

          - Main Valve Body: Cast- or ductile-iron body with AWWA C550 or FDA-approved, interior epoxy coating; or stainless-steel body.

            - Size: <Insert NPS (DN)>.

            - Pattern: [Angle] [Globe]-valve design.

            - Trim: Stainless steel.

          - Design Flow: <Insert gpm (L/s)>.

          - Design Inlet Pressure: <Insert psig (kPa)>.

          - Design Outlet Pressure Setting: <Insert psig (kPa)>.

          - End Connections: Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

      - AUTOMATIC WATER SHUTOFF VALVES

Domestic water automatic shutoff valves below are generally available in NPS 3/4 to NPS 4 (DN 20 to DN 100); verify sizes with manufacturer. Automatic water shutoff valves are most commonly installed in domestic water piping, although they can be used for other applications where moisture detection is desired. Systems include remote water leak sensors to actuate the shutoff valve upon sensing water or possibly temperature. Some systems use a pipe-mounted flow sensor to detect unusual water flow. Variations of the valve are available for water mains, and domestic appliances (clothes washers, domestic water heaters, ice makers, sump pumps, clean rooms, and HVAC system condensate pans). Multiple wired water leak sensors connected to a system allow for wider area coverage. Wireless water leak sensors allow more sensor connections than wired sensors. Relay contacts are used for secondary signaling, device control, and audible alarms.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

          - DynaQuip Controls.

          - FloLogic, Inc.

          - OnSite PRO Inc.

          - <Insert manufacturer's name>.

        - Standards: NSF 61 and NSF 372.

Retain "Shutoff Control Ball Valve" Paragraph below for ball valve sizes NPS 3/4 through NPS 2 (DN 15 through DN 50).

Copy "Shutoff Control Ball Valve" Paragraph and re-edit for each type of shutoff control ball valve required. If only one type is required, drawing designation may be omitted.

        - Shutoff Control Ball Valve <Insert drawing designation if any>:

          - Size: [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] <Insert pipe size>.

          - Design Flow Rate: <Insert gpm (L/s)>.

          - Design Inlet Pressure: <Insert psig (kPa)>.

          - Control Valve: Two-piece, full-port brass ball valve, MSS SP-110.

            - End Connections: Threaded, female.

            - Seats: PTFE.

            - O-Rings: FKM.

            - Stem: Low lead brass. Blowout proof.

            - CWP Rating: [600 psig (4140 kPa)] <Insert pressure>.

          - Manual override control turn-knob for emergency operation of the valve.

Retain "Shutoff Control Butterfly Valve" Paragraph below for butterfly valve sizes NPS 2-1/2 through NPS 4 (DN 65 through DN 100).

Copy "Shutoff Control Butterfly Valve" Paragraph and re-edit for each type of shutoff control butterfly valve required. If only one type is required, drawing designation may be omitted.

        - Shutoff Control Butterfly Valve <Insert drawing designation if any>:

          - Size: [NPS 2-1/2 (DN 65)] [NPS 3 (DN 80)] [NPS 4 (DN 100)] <Insert pipe size>.

          - Compliance: MSS SP-67.

          - Full-port, epoxy-coated, ductile-iron lug body.

          - Seat: EPDM, minus 30 deg F to plus 250 deg F (minus 34 deg C to plus 121 deg C).

          - Face-to-Face Flange: ASME B16.5 flanges.

          - Disc Design: Floating stainless steel dual shaft.

          - Disc Material: [Iron nylon 11] [Stainless steel].

          - Locating Pin: Carbon steel.

          - Bushings: PTFE.

          - O-Rings: EPDM.

          - Ten-position stop.

          - Manual override control turn-knob for emergency operation of the valve.

Retain "Clothes Washer Shutoff Control Valve" Paragraph below for control valves for clothes washers, shutting off both hot- and cold-water supplies.

Copy "Clothes Washer Shutoff Control Valve" Paragraph and re-edit for each type of shutoff control valve required. If only one type is required, drawing designation may be omitted.

        - Clothes Washer Shutoff Control Valve <Insert drawing designation if any>: Two-way, four-port, low-zinc bronze alloy valve.

          - End Connections: Male hose connections, NPS 3/4 (DN 20).

          - Pressure Rating: 400 psi (2758 kPa) at 32 to 150 deg F (0 to 65.6 deg C).

          - Maximum Test Pressure: 1200 psig (8274 kPa).

          - Stem Travel: 0.16 inch (4.0 mm).

          - Maximum Temperature: 250 deg F (121 deg C).

          - Valve Stem: Burnished Type 303 stainless steel.

          - Valve Stem Packing: Double EPDM.

          - Valve Seat: Integral bronze.

          - Valve Disc and Plunger: EPDM.

          - Valve Spring: Stainless steel.

          - Hoses: Two, 9-inch (229-mm) steel braided.

          - Hose End Connections: One straight and one 90-degree elbow connection; both hoses.

Retain "Clothes Washer Shutoff Control Valve Actuator" Paragraph below for control valve actuators for clothes washers, shutting off both hot- and cold-water supplies.

        - Clothes Washer Shutoff Control Valve Actuator: Two position, drive closed, spring open.

          - Housing: High-temperature composite glass-filled nylon.

          - Connection to Valve: NPT female brass ring.

          - Electric Motor: Reversible, brushless, and synchronism, maintains constant control speed to keep the cycle time constant. Maximum stem output is force balance controlled with electronic shutoff when end travel is detected in both directions.

          - Maximum Working Force: 48 lbf (213 N).

          - Power Requirements:

            - Input Voltage: 24 V ac.

            - Frequency: [60] [50] Hz.

            - Current: [0.045] <Insert number> A.

            - Power: [1] <Insert number> VA.

          - Power Supply: 120-to 24-V ac transformer[ with cord and plug].

          - Working Time: [90] <Insert number> seconds.

          - Duty Rating: 100 percent.

          - Travel: 0.16 inch (4.0 mm).

          - Position Indicator: Standard.

          - Working Temperature: 40 to 120 deg F (4.4 to 48.9 deg C).

          - Conform to CE and ROHS requirements.

Retain "Water Main Shutoff Valve Actuator" Paragraph below for ball and butterfly shutoff valves.

        - Water Main Shutoff Valve Actuator: Motor operated, with or without gears, electric and electronic. Capable of closing valve against inlet pressure. Direct mount, two way; fails open/open or closed/closed.

          - Actuator Torque: [133 in. x lbf (15 N x m)] [266 in. x lbf (30 N x m)] <Insert value>.

          - Power Requirements:

            - Input Voltage: [12] [24] V dc.

            - Frequency: [60] [50] Hz.

            - Current: [2] <Insert number> A.

            - Power: [15] [24] <Insert number> VA.

          - Power Supply: 120-V ac to [12] [24]-V dc transformer[ with cord and plug].

          - Working Time: [8] [10] <Insert number> seconds.

          - Torque Limiter: STD.

          - Duty Rating: [50] [75] percent.

          - Protection: [IP65] [IP67].

          - Rotation: [90] [180] degrees.

          - Manual Intervention: Allowed.

          - Position Indicator: Standard.

          - Working Temperature: Minus 4 deg F to plus 131 deg F (Minus 20 deg C to plus 55 deg C).

Retain "Domestic Water Heater Shutoff Valve Actuator" Paragraph below for domestic water heater shutoff valve actuators.

        - Domestic Water Heater Shutoff Valve Actuator: Motor operated, with or without gears, electric and electronic. Capable of closing valve against inlet pressure. Direct mount, two way; fails open/open or close/close.

          - Power Requirements:

            - Input Voltage: 24 V ac.

            - Frequency: [60] [50] Hz.

            - Current: [0.6] <Insert number> A.

            - Power: [15] <Insert number> VA.

          - Power Supply: 120-V ac to 24-V ac transformer[ with cord and plug].

          - Working Time: [45] <Insert number> seconds.

          - Rotation: 90 degrees.

          - Manual Intervention: Allowed.

          - Position Indicator: LED for closed position.

          - Working Temperature: 0 to 100 deg F (Minus 17.8 to plus 37.8 deg C).

          - Audible Alarm: [83] <Insert number> dB.

Retain "Actuator Enclosure" Paragraph below for actuator enclosures.

        - Actuator Enclosure: Suitable for ambient conditions encountered by application.

          - NEMA 250, Type 2 for indoor and protected applications.

          - Material: Self-extinguishing class techno-polymer.

          - <Insert description>.

Retain "Wireless Leak Detection Receiver System" Paragraph below for wireless sensors and coordinate with wired sensor options.

        - Wireless Leak Detection Receiver System:

          - Onboard Battery Backup: 48 hours of protection.[ Valve to close prior to backup failure.]

          - LED Indicators: Wireless signal strength, communication loss, water fault, low temperature fault, and low battery.

          - Output Contacts: Interface with home security or building automation system, cellular text notification service, or auto dialer accessories.

Retain "FCC-Approved Wireless Communication System" Subparagraph below for systems with this capability.

          - FCC-Approved Wireless Communication System: Between devices; sensors, repeaters, and receivers.

            - Proprietary 900-MHz wireless communication platform ensures system operation without Wi-Fi dependence or other communication platforms, subject to power and random service outages.

            - Automatic wireless communication testing and positive confirmation ensure that system devices remain active and working correctly. Automatic fault notification for lost communication or missing device.

          - Power Supply: [120 V ac] [9-V dc battery].

Wireless system can accommodate up to 80 individual sensors; verify with manufacturer.

          - Dual Function Wireless Sensors: [2] <Insert number>.[ Valve closes if temperature falls below 45 deg F (7.2 deg C)].

Specific range may vary due to local structural conditions.

            - Wireless Signal Range: 100 feet (30.5 m) between sensors and receiver.

            - Custom range finding feature.

            - LED Indicators: Wireless signal strength, communication loss, water fault, low temperature, and low battery.

          - Self-monitoring enabled system; faults for lost communication between receiver and sensor(s).

          - Closed-Loop RF System: System remains active even when power and Wi-Fi signals are lost.

Retain "Wired Leak Detection System" Paragraph below for wired sensors and coordinate with wireless sensor options.

        - Wired Leak Detection System: Local water sensor.

          - Power Supply: Class II transformer with cord and plug, 120 V ac, UL listed.

            - Power Cord Length: [12 feet (3.66 m)] <Insert value>.

          - Control Panel: LED power and LED valves indicator.

          - Alarms: Audible alarm[, with external output].

          - Wired Sensors:

            - Quantity Per Receiver: [One] [Two] [Three] [Four] [Five] [Six].

            - Cable Length: [8 feet (2.44 m)] [25 feet (7.62 m)] [50 feet (15.2 m)] [100 feet (30.5 m)] <Insert dimension>.

Retain "Sensor Elevation" Subparagraph below if overflow detection is required, such as HVAC system condensate pans.

          - Sensor Elevation: Elevated [1/2 inch (13 mm)] <Insert dimension> above condensate drain pan.

        - Accessories:

          - Water Flow Sensors: Pipe-mounted to detect water flow.

          - Rope Sensor: Absorbent water sensing rope constructed from twisted metal conductor wires insulated from one another and surrounded by polyethylene mesh braid jacket. Connect up to 100 feet (30.5 m) (10 sections) of sensor rope to a single receiver.

Retain one of first three subparagraphs below for power-vented gas water heaters, requiring that electricity to the power-venter also be shut off when a water leak is detected.

          - Electrical Plug Interrupter: Plugs into standard 120-V ac wall outlet.

          - Gas Flow Interrupter: ECO connector with female spade connectors. Factory prewired, 8 feet (2.44 m).

          - Gas Interface Cable: Interface cable with male and female connectors.

          - Step-Down Transformer: [120] [208] [240] V ac to 24 V ac with mounting plate, 12-foot (3.66-m) plenum wire to power, and 8-foot (2.44-m) plenum wire to sensor.

          - Liquid Level Sensors: Monitor fluid levels in addition to detecting plumbing leaks.

In first subparagraph below, "Auto Dialer" requires a dedicated analog phone line.

          - Auto Dialer: Send and receive automatic alerts when a fault condition occurs. Standard output contacts trigger up to nine predetermined telephone number calls.

            - Prerecord message for future playback.

            - 10-second recordable message.

            - Built-in tamper switch.

            - DC adaptor with battery backup.

            - Programmable as a silent (dialer only) or audible (siren and dialer) alarm.

            - Easy "Stop Call Sequence" - push "#" on phone to acknowledge the alarm and stop the dialing sequence.

In first subparagraph below, "Cellular Text Notification System" requires a mobile wireless network service provider.

          - Cellular Text Notification System.

            - Event SMS text notification to up to three cell phones.

            - Battery Backup: Four (4) AA batteries.

            - 12-foot (3.66-m) interface cable to leak detection system.

            - Customized messaging.

            - <Insert wireless network service provider>.

"Cable Adder" Subparagraph below is for installations that require an additional distance between receiver and shutoff valve.

          - Cable Adder: [10 feet (3 m)] [25 feet (7.62 m)] [50 feet (15.2 m)] [100 feet (30.5 m)] <Insert dimension> in length.

Subparagraphs below are wireless accessories.

          - Wireless Signal Repeater: Boosts signal performance between wireless sensors and receiver.

            - Push-button pairing and unpairing, into and out of the network.

            - Visual indication of wireless signal strength, low battery, and lost communication.

            - Standard wall outlet, 120 V ac, power.

            - Battery Backup: Two (2) AA batteries to maintain system integrity during a power outage.

          - Wireless Water Switch: Allows manual override or wireless system functionality and closes the valve to shut off water flow.

          - Hard-Wired Water Switch: Allows manual override or wireless system functionality and closes the valve to shut off water flow.

      - BALANCING VALVES

Copy "Copper-Alloy Calibrated Balancing Valves" Paragraph below and re-edit for each type of balancing valve required. If only one type is required, drawing designation may be omitted.

        - Copper-Alloy Calibrated Balancing Valves <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Armstrong International, Inc.

            - Flo Fab Inc.

            - ITT Corporation.

            - NIBCO INC.

            - <Insert manufacturer's name>.

          - Type: [Ball] [or] [Y-pattern globe] valve with two readout ports and memory-setting indicator.

          - Body: [Brass] [or] [bronze].

          - Size: Same as connected piping, but not larger than NPS 2 (DN 50).

          - Accessories: Meter hoses, fittings, valves, differential pressure meter, and carrying case.

Copy "Cast-Iron Calibrated Balancing Valves" Paragraph below and re-edit for each type of balancing valve required. If only one type is required, drawing designation may be omitted.

        - Cast-Iron Calibrated Balancing Valves <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Armstrong International, Inc.

            - Flo Fab Inc.

            - ITT Corporation.

            - NIBCO INC.

            - <Insert manufacturer's name>.

          - Type: Adjustable with Y-pattern globe valve, two readout ports, and memory-setting indicator.

          - Size: Same as connected piping, but not smaller than NPS 2-1/2 (DN 65).

        - Accessories: Meter hoses, fittings, valves, differential pressure meter, and carrying case.

Copy "Memory-Stop Balancing Valves" Paragraph below and re-edit for each type of balancing valve required. If only one type is required, drawing designation may be omitted.

        - Memory-Stop Balancing Valves <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - Crane; Crane Energy Flow Solutions.

            - Hammond Valve.

            - Jenkins Valves; Crane Energy Flow Solutions.

            - Milwaukee Valve Company.

            - NIBCO INC.

            - <Insert manufacturer's name>.

          - Standard: MSS SP-110 for two-piece, copper-alloy ball valves.

          - Pressure Rating: 400-psig (2760-kPa) minimum CWP.

          - Size: NPS 2 (DN 50) or smaller.

          - Body: Copper alloy.

          - Port: Standard or full port.

          - Ball: Chrome-plated brass.

          - Seats and Seals: Replaceable.

          - End Connections: Solder joint or threaded.

          - Handle: Vinyl-covered steel with memory-setting device.

      - TEMPERATURE-ACTUATED, WATER MIXING VALVES

Copy "Water-Temperature Limiting Devices" Paragraph below and re-edit for each type of limiting device required. If only one type is required, drawing designation may be omitted.

Water-temperature limiting devices in first paragraph below are unsuitable for service as master thermostatic mixing valves. Devices below are available in NPS 1/2 to NPS 1 (DN 15 to DN 25) and comply with ASSE 1016, ASSE 1017, or both; however, neither standard is adequate for them. ASSE 1070, "Performance Requirements for Water Temperature Limiting Devices," is under development.

        - Water-Temperature Limiting Devices <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - Armstrong International, Inc.

            - Cash Acme; a division of Reliance Worldwide Corporation.

            - Honeywell.

            - Legend Valve & Fitting, Inc.

            - Leonard Valve Company.

            - POWERS; a WATTS brand.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1017.

          - Pressure Rating: 125 psig (860 kPa).

          - Type: Thermostatically controlled, water mixing valve.

          - Material: Bronze body with corrosion-resistant interior components.

          - Connections: Threaded[ union] inlets and outlet.

          - Accessories: Check stops on hot- and cold-water supplies, and adjustable, temperature-control handle.

          - Tempered-Water Setting: <Insert deg F (deg C)>.

Retain "Tempered-Water Design Flow Rate" Subparagraph below only if flow rate is not indicated on Drawings.

          - Tempered-Water Design Flow Rate: <Insert gpm (L/s)>.

          - Valve Finish: [Chrome plated] [Rough bronze].

Copy "Primary, Thermostatic, Water Mixing Valves" Paragraph below and re-edit for each type of water mixing valve required. If only one type is required, drawing designation may be omitted.

Primary, thermostatic, water mixing valves in first paragraph below are available in NPS 3/4 to NPS 3 and maybe in NPS 4 (DN 20 to DN 80 and maybe in DN 100), but usually are NPS 2 (DN 50) or smaller.

        - Primary, Thermostatic, Water Mixing Valves <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Acorn Engineering Company.

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - Armstrong International, Inc.

            - Cash Acme, a division of Reliance Worldwide Corporation.

            - Lawler Manufacturing Company, Inc.

            - Leonard Valve Company.

            - POWERS; a WATTS brand.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1017.

          - Pressure Rating: 125 psig (860 kPa) minimum unless otherwise indicated.

          - Type: [Exposed-mounted] [Cabinet-type], thermostatically controlled, water mixing valve.

          - Material: Bronze body with corrosion-resistant interior components.

          - Connections: Threaded[ union] inlets and outlet.

          - Accessories: Manual temperature control, check stops on hot- and cold-water supplies, and adjustable, temperature-control handle.

          - Tempered-Water Setting: <Insert deg F (deg C)>.

Retain "Tempered-Water Design Flow Rate" Subparagraph below only if flow rate is not indicated on Drawings.

          - Tempered-Water Design Flow Rate: <Insert gpm (L/s)>.

          - Selected Valve Flow Rate at 45-psig (310-kPa) Pressure Drop: <Insert gpm (L/s)>.

          - Pressure Drop at Design Flow Rate: <Insert psig (kPa)>.

          - Valve Finish: [Chrome plated] [Polished, chrome plated] [Rough bronze].

          - Piping Finish: [Chrome plated] [Copper].

Retain "Cabinet" Subparagraph below if cabinet is required.

          - Cabinet: Factory fabricated, stainless steel, for [recessed] [surface] mounting and with hinged, stainless steel door.

Copy "Manifold, Thermostatic, Water Mixing-Valve Assemblies" Paragraph below and re-edit for each type of water mixing-valve assembly required. If only one type is required, drawing designation may be omitted.

Several manufacturers of thermostatic mixing valves promote single "high-low" valves to be used instead of the manifold valve assemblies in first paragraph below. If single valves are required for high and low systems, specify them in "Primary, Thermostatic, Water Mixing Valves" Paragraph.

        - Manifold, Thermostatic, Water Mixing-Valve Assemblies <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Leonard Valve Company.

            - POWERS; a WATTS brand.

            - <Insert manufacturer's name>.

          - Description: Factory-fabricated, [cabinet-type] [exposed-mounted], thermostatically controlled, water mixing-valve assembly in [two] [three]-valve parallel arrangement.

          - Large-Flow Parallel: Thermostatic, water mixing valve and downstream-pressure regulator with pressure gages on inlet and outlet.

Retain "Intermediate-Flow Parallel" Subparagraph below for three-valve assemblies.

          - Intermediate-Flow Parallel: Thermostatic, water mixing valve and downstream-pressure regulator with pressure gages on inlet and outlet.

          - Small-Flow Parallel: Thermostatic, water mixing valve.

          - Thermostatic Mixing Valves: Comply with ASSE 1017. Include check stops on hot- and cold-water inlets and shutoff valve on outlet.

          - Water Regulator(s): Comply with ASSE 1003. Include pressure gage on inlet and outlet.

          - Pressure Rating: 125 psig (860 kPa) minimum unless otherwise indicated.

Retain "Cabinet" Subparagraph below for cabinet-type assembly.

          - Cabinet: Factory fabricated, stainless steel, for [recessed] [surface] mounting and with hinged, stainless-steel door.

          - Selected Large-Flow, Tempered-Water Valve Size: <Insert size>.

          - Tempered-Water Setting: <Insert deg F (deg C)>.

          - Unit Tempered-Water Design Flow Rate: <Insert gpm (L/s)>.

          - Unit Minimum Tempered-Water Design Flow Rate: <Insert gpm (L/s)>.

          - Selected Unit Flow Rate at 45-psig (310-kPa) Pressure Drop: <Insert gpm (L/s)>.

          - Unit Pressure Drop at Design Flow Rate: <Insert psig (kPa)>.

          - Unit Tempered-Water Outlet Size: <Insert NPS (DN)> end connection.

          - Unit Hot- and Cold-Water Inlet Size: <Insert NPS (DN)> end connections.

          - Thermostatic Mixing Valve and Water Regulator Finish: [Chrome plated] [Polished, chrome plated] [Rough bronze].

          - Piping Finish: [Chrome plated] [Copper].

Copy "Photographic-Process, Thermostatic, Water Mixing-Valve Assemblies" Paragraph below and re-edit for each type of water mixing-valve assembly required. If only one type is required, drawing designation may be omitted.

        - Photographic-Process, Thermostatic, Water Mixing-Valve Assemblies <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Lawler Manufacturing Company, Inc.

            - Leonard Valve Company.

            - POWERS; a WATTS brand.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1017, thermostatically controlled, water mixing valve made for precise, process-water temperature control.

          - Pressure Rating: 125 psig (860 kPa) minimum unless otherwise indicated.

          - Body: Bronze with corrosion-resistant interior components.

          - Connections: Threaded inlets and outlet.

          - Accessories: Manual temperature control, check stops on hot- and cold-water supplies, thermometer, shutoff valve, and adjustable, temperature-control handle.

          - Cabinet: Factory fabricated, stainless steel, for surface mounting; with controls and thermometer mounted on front.

          - Tempered-Water Setting: <Insert deg F (deg C)>.

          - Tempered-Water Design Flow Rate: <Insert gpm (L/s)>.

          - Tempered-Water Outlet Size: <Insert NPS (DN)> end connection.

          - Hot- and Cold-Water Inlet Size: <Insert NPS (DN)> end connections.

Copy "Individual-Fixture, Water Tempering Valves" Paragraph below and re-edit for each type of water tempering valve required. If only one type is required, drawing designation may be omitted.

Individual-fixture, water tempering valves in first paragraph below are unsuitable for service as primary water tempering valves. Valves below are available in NPS 3/4 (DN 20) and larger; however, devices in "Water-Temperature Limiting Devices" Paragraph should be used instead.

        - Individual-Fixture, Water Tempering Valves <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Acorn Engineering Company.

            - Apollo Flow Controls; Conbraco Industries, Inc.

            - Cash Acme; a division of Reliance Worldwide Corporation.

            - Honeywell.

            - Lawler Manufacturing Company, Inc.

            - Leonard Valve Company.

            - POWERS; a WATTS brand.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1016, thermostatically controlled, water tempering valve.

          - Pressure Rating: 125 psig (860 kPa) minimum unless otherwise indicated.

          - Body: Bronze body with corrosion-resistant interior components.

          - Temperature Control: Adjustable.

          - Inlets and Outlet: Threaded.

          - Finish: Rough or chrome-plated bronze.

          - Tempered-Water Setting: <Insert deg F (deg C)>.

Retain "Tempered-Water Design Flow Rate" Subparagraph below only if required.

          - Tempered-Water Design Flow Rate: <Insert gpm (L/s)>.

Copy "Primary Water Tempering Valves" Paragraph below and re-edit for each type of water tempering valve required. If only one type is required, drawing designation may be omitted.

Primary water tempering valves in paragraph below are available in NPS 1/2 to NPS 4 (DN 15 to DN 100).

        - Primary Water Tempering Valves <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Heat-Timer Corporation.

            - Holby Valve Inc.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1017, thermostatically controlled, water tempering valve, listed as tempering valve.

          - Pressure Rating: 125 psig (860 kPa) minimum unless otherwise indicated.

          - Body: Bronze.

          - Temperature Control: Manual.

          - Inlets and Outlet: Threaded.

          - Selected Primary Water Tempering Valve Size: <Insert size>.

          - Tempered-Water Setting: <Insert deg F (deg C)>.

          - Tempered-Water Design Flow Rate: <Insert gpm (L/s)>.

          - Pressure Drop at Design Flow Rate: <Insert psig (kPa)>.

          - Tempered-Water Outlet Size: <Insert NPS (DN)> end connection.

          - Cold-Water Inlet Size: <Insert NPS (DN)> end connection.

          - Hot-Water Inlet Size: <Insert NPS (DN)> end connection.

          - Valve Finish: [Rough bronze] <Insert finish>.

      - STRAINERS FOR DOMESTIC WATER PIPING

Copy "Y-Pattern Strainers" Paragraph below and re-edit for each type of Y-pattern strainer required. If only one type is required, drawing designation may be omitted.

        - Y-Pattern Strainers <Insert drawing designation if any>:

          - Pressure Rating: 125 psig (860 kPa) minimum unless otherwise indicated.

          - Body: Bronze for NPS 2 (DN 50) and smaller; cast iron[ with interior lining that complies with AWWA C550 or that is FDA approved, epoxy coated and] for NPS 2-1/2 (DN 65) and larger.

          - End Connections: Threaded for NPS 2 (DN 50) and smaller; flanged for NPS 2-1/2 (DN 65) and larger.

          - Screen: Stainless steel with round perforations unless otherwise indicated.

If retaining more than one screen size, indicate screen size on Drawings.

          - Perforation Size:

            - Strainers NPS 2 (DN 50) and Smaller: [0.020 inch (0.51 mm)] [0.033 inch (0.84 mm)] [0.062 inch (1.57 mm)] <Insert dimension>.

            - Strainers NPS 2-1/2 to NPS 4 (DN 65 to DN 100): [0.045 inch (1.14 mm)] [0.062 inch (1.57 mm)] [0.125 inch (3.18 mm)] <Insert dimension>.

            - Strainers NPS 5 (DN 125) and Larger: [0.10 inch (2.54 mm)] [0.125 inch (3.18 mm)] [0.25 inch (6.35 mm)] <Insert dimension>.

          - Drain: [Pipe plug] [Factory-installed, hose-end drain valve].

      - OUTLET BOXES

Authorities having jurisdiction may require backflow preventers in water-supply piping or on hose-thread outlets.

Copy "Clothes Washer Outlet Boxes PVC" Paragraph below and re-edit for each type of outlet box required. If only one type is required, drawing designation may be omitted.

        - Clothes Washer Outlet Boxes, PVC <Insert drawing designation if any>:

For product information about Oatey’s; "Centro II Washing Machine Outlet Boxes", see www.oatey.com/ASSETS/DOCUMENTS/ITEMS/EN/centro-wmob-ii-submittal.pdf.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Oatey; Centro II Washing Machine Outlet Boxes or comparable product by one of the following:

            - Acorn Engineering Company.

            - Guy Gray Manufacturing Co., Inc.

            - IPS Corporation.

            - LSP Products Group, Inc.

            - Plastic Oddities.

            - <Insert manufacturer's name>.

          - Mounting: Recessed.

          - Material and Finish: PVC box and faceplate.

          - Faucet: Combination valved fitting or separate hot- and cold-water valved fittings complying with ASME A112.18.1. Include garden-hose thread complying with ASME B1.20.7 on outlets.

          - Supply Shutoff Fittings: NPS 1/2 (DN 15) gate, globe, or ball valves and NPS 1/2 (DN 15) copper, water tubing.

          - Drain: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] standpipe and P-trap for direct waste connection to drainage piping.

Retain "Inlet Hoses" or "Drain Hose" Subparagraph below, or both, if required. Hoses are usually included with clothes washers.

          - Inlet Hoses: Two 60-inch- (1500-mm-) long, rubber household clothes washer inlet hoses with female, garden-hose-thread couplings. Include rubber washers.

          - Drain Hose: One 48-inch- (1200-mm-) long, rubber household clothes washer drain hose with hooked end.

Copy "Clothes Washer Outlet Boxes, Fire Rated" Paragraph below and re-edit for each type of outlet box required. If only one type is required, drawing designation may be omitted.

        - Clothes Washer Outlet Boxes, Fire-Rated <Insert drawing designation if any>:

For product information about Oatey’s "Fire-Rated Washing Machine Outlet Boxes", see www.oatey.com/ASSETS/DOCUMENTS/ITEMS/EN/FIRE%20WMOB.pdf.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Oatey; Fire-Rated Washing Machine Outlet Boxes or comparable product by one of the following:

            - Acorn Engineering Company.

            - Guy Gray Manufacturing Co., Inc.

            - IPS Corporation.

            - LSP Products Group, Inc.

            - Plastic Oddities.

            - <Insert manufacturer's name>.

          - Mounting: Recessed.

          - Material and Finish: PVC box and faceplate.

          - Faucet: Combination valved fitting or separate hot- and cold-water valved fittings complying with ASME A112.18.1. Include garden-hose thread complying with ASME B1.20.7 on outlets.

          - Supply Shutoff Fittings: NPS 1/2 (DN 15) gate, globe, or ball valves and NPS 1/2 (DN 15) copper, water tubing.

          - Drain: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] standpipe and P-trap for direct waste connection to drainage piping.

Retain "Inlet Hoses" or "Drain Hose" Subparagraph below, or both, if required. Hoses are usually included with clothes washers.

          - Inlet Hoses: Two 60-inch- (1500-mm-) long, rubber household clothes washer inlet hoses with female, garden-hose-thread couplings. Include rubber washers.

          - Drain Hose: One 48-inch- (1200-mm-) long, rubber household clothes washer drain hose with hooked end.

Copy "Clothes Washer Outlet Boxes, Metal" Paragraph below and re-edit for each type of outlet box required. If only one type is required, drawing designation may be omitted.

        - Clothes Washer Outlet Boxes, Metal <Insert drawing designation if any>:

For product information about Oatey’s "Metal Washing Machine Outlet Boxes", see www.oatey.com/ASSETS/DOCUMENTS/ITEMS/EN/Metal_WMOB_Submittal.pdf .

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Oatey; Metal Washing Machine Outlet Boxes or comparable product by one of the following:

            - Acorn Engineering Company.

            - Guy Gray Manufacturing Co., Inc.

            - IPS Corporation.

            - LSP Products Group, Inc.

            - Plastic Oddities.

            - <Insert manufacturer's name>.

          - Mounting: Recessed.

          - Material and Finish: 20-gauge, 0.0375-inch (0.95-mm) box and 18 gauge, 0.05-inch (1.27-mm) faceplate.

          - Faucet: Combination valved fitting or separate hot- and cold-water valved fittings complying with ASME A112.18.1. Include garden-hose thread complying with ASME B1.20.7 on outlets.

          - Supply Shutoff Fittings: NPS 1/2 (DN 15) gate, globe, or ball valves and NPS 1/2 (DN 15) copper, water tubing.

          - Drain: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] standpipe and P-trap for direct waste connection to drainage piping.

Retain "Inlet Hoses" or "Drain Hose" Subparagraph below, or both, if required. Hoses are usually included with clothes washers.

          - Inlet Hoses: Two 60-inch- (1500-mm-) long, rubber household clothes washer inlet hoses with female, garden-hose-thread couplings. Include rubber washers.

          - Drain Hose: One 48-inch- (1200-mm-) long, rubber household clothes washer drain hose with hooked end.

Copy "Clothes Washer Outlet Boxes, Modular" Paragraph below and re-edit for each type of outlet box required. If only one type is required, drawing designation may be omitted.

        - Clothes Washer Outlet Boxes, Modular <Insert drawing designation if any>:

For product information about Oatey’s "Modular Wash Machine Outlet Boxes", see https://www.oatey.com/ASSETS/DOCUMENTS/ITEMS/EN/ModaSpecifications_WashingMachineOutletBox.pdf.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Oatey; Moda Washing Machine Outlet Boxes or comparable product by one of the following:

            - Acorn Engineering Company.

            - Guy Gray Manufacturing Co., Inc.

            - IPS Corporation.

            - LSP Products Group, Inc.

            - Plastic Oddities.

            - <Insert manufacturer's name>.

          - Mounting: Recessed.

          - Material and Finish: PVC box and faceplate.

          - Faucet: Combination valved fitting or separate hot- and cold-water valved fittings complying with ASME A112.18.1. Include garden-hose thread complying with ASME B1.20.7 on outlets.

          - Supply Shutoff Fittings: NPS 1/2 (DN 15) gate, globe, or ball valves and NPS 1/2 (DN 15) copper, water tubing.

          - Drain: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] standpipe and P-trap for direct waste connection to drainage piping.

Retain "Inlet Hoses" or "Drain Hose" Subparagraph below, or both, if required. Hoses are usually included with clothes washers.

          - Inlet Hoses: Two 60-inch- (1500-mm-) long, rubber household clothes washer inlet hoses with female, garden-hose-thread couplings. Include rubber washers.

          - Drain Hose: One 48-inch- (1200-mm-) long, rubber household clothes washer drain hose with hooked end.

Copy "Icemaker Outlet Boxes, Fire-Rated" Paragraph below and re-edit for each type of outlet box required. If only one type is required, drawing designation may be omitted.

        - Icemaker Outlet Boxes, Fire-Rated <Insert drawing designation if any>:

For product information about Oatey’s "Fire-Rated Icemaker Outlet Boxes", see www.oatey.com/ASSETS/DOCUMENTS/ITEMS/EN/fire-imob.pdf.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Oatey; Fire-Rated Icemaker Outlet Boxes or comparable product by one of the following:

            - Acorn Engineering Company.

            - IPS Corporation.

            - LSP Products Group, Inc.

            - Plastic Oddities.

            - <Insert manufacturer's name>.

          - Mounting: Recessed.

          - Material and Finish: PVC box and faceplate.

          - Faucet: Valved fitting complying with ASME A112.18.1. Include NPS 1/2 (DN 15) or smaller copper tube outlet.

          - Supply Shutoff Fitting: NPS 1/2 (DN 15) gate, globe, or ball valve and NPS 1/2 (DN 15) copper, water tubing.

Copy "Icemaker Outlet Boxes, Metal" Paragraph below and re-edit for each type of outlet box required. If only one type is required, drawing designation may be omitted.

        - Icemaker Outlet Boxes, Metal <Insert drawing designation if any>:

For product information about Oatey’s "Fire-Rated Icemaker Outlet Boxes", see www.oatey.com/ASSETS/DOCUMENTS/ITEMS/EN/Metal20IMB2.pdf.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Oatey; Metal Icemaker Outlet Boxes or comparable product by one of the following:

            - Acorn Engineering Company.

            - IPS Corporation.

            - LSP Products Group, Inc.

            - Plastic Oddities.

            - <Insert manufacturer's name>.

          - Mounting: Recessed.

          - Material and Finish: Galvanized steel with powder-coated white finish box and faceplate.

          - Faucet: Valved fitting complying with ASME A112.18.1. Include NPS 1/2 (DN 15) or smaller copper tube outlet.

          - Supply Shutoff Fitting: NPS 1/2 (DN 15) gate, globe, or ball valve and NPS 1/2 (DN 15) copper, water tubing.

Copy "Icemaker Outlet Boxes, Modular" Paragraph below and re-edit for each type of outlet box required. If only one type is required, drawing designation may be omitted.

        - Icemaker Outlet Boxes, Modular <Insert drawing designation if any>:

For product information about Oatey’s "Modular Icemaker Outlet Boxes", see https://www.oatey.com/ASSETS/DOCUMENTS/ITEMS/EN/ModaSpecifications_IceMakerSupplyBox.pdf.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Oatey; Moda Icemaker Outlet Boxes or comparable product by one of the following:

            - Acorn Engineering Company.

            - IPS Corporation.

            - LSP Products Group, Inc.

            - Plastic Oddities.

            - <Insert manufacturer's name>.

          - Mounting: Recessed.

          - Material and Finish: PVC box and faceplate.

          - Faucet: Valved fitting complying with ASME A112.18.1. Include NPS 1/2 (DN 15) or smaller copper tube outlet.

          - Supply Shutoff Fitting: NPS 1/2 (DN 15) gate, globe, or ball valve and NPS 1/2 (DN 15) copper, water tubing.

Copy "Kitchen Outlet Boxes, Modular" Paragraph below and re-edit for each type of outlet box required. If only one type is required, drawing designation may be omitted.

        - Kitchen Outlet Boxes, Modular <Insert drawing designation if any>:

For product information about Oatey’s "Modular Kitchen Outlet Boxes", see https://www.oatey.com/ASSETS/DOCUMENTS/ITEMS/EN/ModaSpecifications_KitchenSupplyBox.pdf.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Oatey; Moda Kitchen Outlet Boxes or comparable product by one of the following:

            - Acorn Engineering Company.

            - IPS Corporation.

            - LSP Products Group, Inc.

            - Plastic Oddities.

            - <Insert manufacturer's name>.

          - Mounting: Recessed.

          - Material and Finish: PVC box and faceplate.

          - Faucet: Valved fitting complying with ASME A112.18.1. Include NPS 1/2 (DN 15) or smaller copper tube outlet.

          - Supply Shutoff Fitting: NPS 1/2 (DN 15) gate, globe, or ball valve and NPS 1/2 (DN 15) copper, water tubing.

Copy "Lavatory Outlet Boxes, Modular" Paragraph below and re-edit for each type of outlet box required. If only one type is required, drawing designation may be omitted.

        - Lavatory Outlet Boxes, Modular <Insert drawing designation if any>:

For product information about Oatey’s "Modular Lavatory Outlet Boxes", see https://www.oatey.com/ASSETS/DOCUMENTS/ITEMS/EN/ModaSpecifications_LavatorySupplyBox.pdf.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Oatey; Moda Lavatory Outlet Boxes or comparable product by one of the following:

            - Acorn Engineering Company.

            - IPS Corporation.

            - LSP Products Group, Inc.

            - Plastic Oddities.

            - <Insert manufacturer's name>.

          - Mounting: Recessed.

          - Material and Finish: PVC box and faceplate.

          - Faucet: Valved fitting complying with ASME A112.18.1. Include NPS 1/2 (DN 15) or smaller copper tube outlet.

          - Supply Shutoff Fitting: NPS 1/2 (DN 15) gate, globe, or ball valve and NPS 1/2 (DN 15) copper, water tubing.

Copy "Toilet/Dishwasher Outlet Boxes, Modular" Paragraph below and re-edit for each type of outlet box required. If only one type is required, drawing designation may be omitted.

        - Toilet/Dishwasher Outlet Boxes, Modular <Insert drawing designation if any>:

For product information about Oatey’s "Modular Toilet/Dishwasher Outlet Boxes", see https://www.oatey.com/ASSETS/DOCUMENTS/ITEMS/EN/ModaSpecifications_ToiletSupplyBox.pdf.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Oatey; Moda Toilet/Dishwasher Outlet Boxes or comparable product by one of the following:

            - Acorn Engineering Company.

            - IPS Corporation.

            - LSP Products Group, Inc.

            - Plastic Oddities.

            - <Insert manufacturer's name>.

          - Mounting: Recessed.

          - Material and Finish: PVC box and faceplate.

          - Faucet: Valved fitting complying with ASME A112.18.1. Include NPS 1/2 (DN 15) or smaller copper tube outlet.

          - Supply Shutoff Fitting: NPS 1/2 (DN 15) gate, globe, or ball valve and NPS 1/2 (DN 15) copper, water tubing.

Copy "Air Admittance Valve Outlet Boxes" Paragraph below and re-edit for each type of outlet box required. If only one type is required, drawing designation may be omitted.

        - Air Admittance Valve Outlet Boxes, <Insert drawing designation if any>:

For product information about Oatey’s "Modular Air Admittance Valve Outlet Boxes", see https://www.oatey.com/ASSETS/DOCUMENTS/ITEMS/.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Oatey; SureVent Air Admittance Valve Wall Boxes or comparable product by one of the following:

            - Acorn Engineering Company.

            - IPS Corporation.

            - LSP Products Group, Inc.

            - Plastic Oddities.

            - <Insert manufacturer's name>.

          - Mounting: Recessed.

          - Material and Finish: PVC box and faceplate.

          - Faucet: Valved fitting complying with ASME A112.18.1. Include NPS 1/2 (DN 15) or smaller copper tube outlet.

          - Supply Shutoff Fitting: NPS 1/2 (DN 15) gate, globe, or ball valve and NPS 1/2 (DN 15) copper, water tubing.

Copy "Wall Outlet Boxes" Paragraph below and re-edit for each type of outlet box required. If only one type is required, drawing designation may be omitted.

        - Wall Outlet Boxes,<Insert drawing designation if any>:

For product information about Oatey’s "Modular SureVent WallOutlet Boxes", see https://www.oatey.com/ASSETS/DOCUMENTS/ITEMS.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Oatey; SureVent Boxes or comparable product by one of the following:

            - Acorn Engineering Company.

            - IPS Corporation.

            - LSP Products Group, Inc.

            - Plastic Oddities.

            - <Insert manufacturer's name>.

          - Mounting: Recessed.

          - Material and Finish: PVC box and faceplate.

          - Faucet: Valved fitting complying with ASME A112.18.1. Include NPS 1/2 (DN 15) or smaller copper tube outlet.

          - Supply Shutoff Fitting: NPS 1/2 (DN 15) gate, globe, or ball valve and NPS 1/2 (DN 15) copper, water tubing.

      - HOSE STATIONS

Authorities having jurisdiction may require backflow preventers in water-supply piping or on hose-thread outlets. Revise this article to suit Project.

Copy "Single-Temperature-Water Hose Stations" Paragraph below and re-edit for each type of hose station required. If only one type is required, drawing designation may be omitted.

        - Single-Temperature-Water Hose Stations <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - ARCHON Industries, Inc.

            - Armstrong International, Inc.

            - Cooney Brothers, Inc.

            - DynaFluid Ltd.

            - Leonard Valve Company.

            - <Insert manufacturer's name>.

          - Standard: ASME A112.18.1.

          - Cabinet: Stainless steel enclosure with exposed valve handle, hose connection, and hose rack. Include thermometer in front.

          - Hose-Rack Material: Stainless steel.

          - Body Material: Bronze[ with stainless steel wetted parts].

          - Body Finish: Rough bronze[, chrome plated].

          - Mounting: [Wall, with reinforcement] [Floor, with stainless steel pedestal].

          - Supply Fittings: [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] gate, globe, or ball valve and check valve and [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] copper, water tubing. Omit check valve if check stop is included with fitting.

          - Hose: Manufacturer's standard, for service fluid, temperature, and pressure; [25 feet (7.6 m)] [50 feet (15 m)] <Insert dimension> long.

          - Nozzle: With hand-squeeze, on-off control.

          - Vacuum Breaker:

            - Integral or factory-installed, nonremovable, manual-drain-type, hose-connection vacuum breaker complying with ASSE 1011 or backflow preventer complying with ASSE 1052.

            - Garden-hose thread complying with ASME B1.20.7 on outlet.

Copy "Hot- and Cold-Water Hose Stations" Paragraph below and re-edit for each type of hose station required. If only one type is required, drawing designation may be omitted.

        - Hot- and Cold-Water Hose Stations <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - ARCHON Industries, Inc.

            - Armstrong International, Inc.

            - Cooney Brothers, Inc.

            - DynaFluid Ltd.

            - Leonard Valve Company.

            - <Insert manufacturer's name>.

          - Standard: ASME A112.18.1.

          - Faucet Type: [Blending] [Thermostatic mixing] valve.

          - Cabinet: Stainless-steel enclosure with exposed valve handles, hose connection, and hose rack. Include thermometer in front.

          - Hose-Rack Material: Stainless steel.

          - Body Material: Bronze[ with stainless steel wetted parts].

          - Body Finish: Rough bronze[ or chrome plated].

          - Mounting: [Wall, with reinforcement] [Floor, with stainless steel pedestal].

          - Supply Fittings: Two [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] gate, globe, or ball valves and check valves and [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] copper, water tubing. Omit check valves if check stops are included with fitting.

          - Hose: Manufacturer's standard, for service fluid, temperature, and pressure; [25 feet (7.6 m)] [50 feet (15 m)] <Insert dimension> long.

          - Nozzle: With hand-squeeze, on-off control.

          - Vacuum Breaker: Integral or factory-installed, nonremovable, manual-drain-type, hose-connection vacuum breaker complying with ASSE 1011 or backflow preventer complying with ASSE 1052; and garden-hose thread complying with ASME B1.20.7 on outlet.

Copy "Cold-Water and Steam Hose Stations" Paragraph below and re-edit for each type of hose station required. If only one type is required, drawing designation may be omitted.

        - Cold-Water and Steam Hose Stations <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - ARCHON Industries, Inc.

            - Armstrong International, Inc.

            - Cooney Brothers, Inc.

            - DynaFluid Ltd.

            - Leonard Valve Company.

            - <Insert manufacturer's name>.

          - Standard: ASME A112.18.1.

          - Faucet Type: [Blending] [Thermostatic mixing] valve.

          - Cabinet: Stainless-steel enclosure with exposed valve handles, hose connection, and hose rack. Include thermometer in front.

          - Hose-Rack Material: Stainless steel.

          - Body Material: Bronze[ with stainless steel wetted parts].

          - Body Finish: Rough bronze[ or chrome plated].

          - Mounting: [Wall, with reinforcement] [Floor, with stainless steel pedestal].

          - Supply Fittings: Two [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] gate, globe, or ball valves and check valves and [NPS 1/2 (DN 15)] [NPS 3/4 (DN 20)] copper, water tubing. Omit check valves if check stops are included with fitting.

          - Hose: Manufacturer's standard, for service fluid, temperature, and pressure; [25 feet (7.6 m)] [50 feet (15 m)] <Insert dimension> long.

          - Nozzle: With hand-squeeze, on-off control.

          - Vacuum Breaker:

            - Integral or factory-installed, nonremovable, manual-drain-type, hose-connection vacuum breaker complying with ASSE 1011 or backflow preventer complying with ASSE 1052.

            - Garden-hose thread complying with ASME B1.20.7 on outlet.

      - HOSE BIBBS

Copy "Hose Bibbs" Paragraph below for each type of hose bibb required. If only one type is required, drawing designation may be omitted.

        - Hose Bibbs <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Jay R. Smith Mfg. Co.

            - Josam Company.

            - MIFAB, Inc.

            - Prier Products, Inc.

            - <Insert manufacturer's name>.

          - Standard: ASME A112.18.1 for sediment faucets.

          - Body Material: Bronze.

          - Seat: Bronze, replaceable.

          - Supply Connections: NPS 1/2 or NPS 3/4 (DN 15 or DN 20) threaded or solder-joint inlet.

          - Outlet Connection: Garden-hose thread complying with ASME B1.20.7.

          - Pressure Rating: 125 psig (860 kPa).

          - Vacuum Breaker: Integral[ or field-installation,] nonremovable, drainable, hose-connection vacuum breaker complying with ASSE 1011.

          - Finish for Equipment Rooms: Rough bronze, or chrome or nickel plated.

          - Finish for Service Areas: [Rough bronze] [Chrome or nickel plated].

          - Finish for Finished Rooms: Chrome or nickel plated.

          - Operation for Equipment Rooms: Wheel handle or operating key.

          - Operation for Service Areas: [Wheel handle] [Operating key].

          - Operation for Finished Rooms: [Wheel handle] [Operating key].

          - Include operating key with each operating-key hose bibb.

          - Include[ integral] wall flange with each chrome- or nickel-plated hose bibb.

      - WALL HYDRANTS

Wall hydrants without integral vacuum breakers or backflow preventers are available but not recommended.

Copy "Nonfreeze Wall Hydrants" Paragraph below for each type of wall hydrant required. If only one type is required, drawing designation may be omitted.

        - Nonfreeze Wall Hydrants <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Jay R. Smith Mfg. Co.

            - Josam Company.

            - MIFAB, Inc.

            - Prier Products, Inc.

            - <Insert manufacturer's name>.

          - Standard: ASME A112.21.3M for [concealed] [exposed]-outlet, self-draining wall hydrants.

          - Pressure Rating: 125 psig (860 kPa).

          - Operation: Loose key.

          - Casing and Operating Rod: Of length required to match wall thickness. Include wall clamp.

          - Inlet: NPS 3/4 or NPS 1 (DN 20 or DN 25).

          - Outlet: Concealed, with integral vacuum breaker and garden-hose thread complying with ASME B1.20.7.

          - Box: Deep, flush mounted with cover.

          - Box and Cover Finish: [Polished nickel bronze] [Chrome plated] <Insert finish>.

Retain "Outlet," "Box," and "Box and Cover Finish" subparagraphs above for concealed-outlet-type wall hydrants or "Outlet" and "Nozzle and Wall-Plate Finish" subparagraphs below for exposed-outlet-type wall hydrants.

          - Outlet: Exposed, with integral vacuum breaker and garden-hose thread complying with ASME B1.20.7.

          - Nozzle and Wall-Plate Finish: [Polished nickel bronze] [Rough bronze] <Insert finish>.

          - Operating Keys(s): [One] [Two] with each wall hydrant.

Copy "Nonfreeze, Hot- and Cold-Water Wall Hydrants" Paragraph below and re-edit for each type of wall hydrant required. If only one type is required, drawing designation may be omitted.

        - Nonfreeze, Hot- and Cold-Water Wall Hydrants <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Jay R. Smith Mfg. Co.

            - Josam Company.

            - Prier Products, Inc.

            - <Insert manufacturer's name>.

          - Standard: ASME A112.21.3M for [concealed] [exposed]-outlet, self-draining wall hydrants.

          - Pressure Rating: 125 psig (860 kPa).

          - Operation: Loose key.

          - Casing and Operating Rods: Of length required to match wall thickness. Include wall clamps.

          - Inlet: NPS 3/4 or NPS 1 (DN 20 or DN 25).

          - Outlet: Concealed.

          - Box: Deep, flush mounted with cover.

          - Box and Cover Finish: [Polished nickel bronze] [Chrome plated] <Insert finish>.

          - Vacuum Breaker:

            - Nonremovable, manual-drain-type, hose-connection vacuum breaker complying with ASSE 1011 or backflow preventer complying with ASSE 1052.

            - Garden-hose thread complying with ASME B1.20.7 on outlet.

          - Operating Key(s): [One] [Two] with each wall hydrant.

Copy "Moderate-Climate Wall Hydrants" Paragraph below and re-edit for each type of wall hydrant required. If only one type is required, drawing designation may be omitted.

        - Moderate-Climate Wall Hydrants <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Jay R. Smith Mfg. Co.

            - Josam Company.

            - MIFAB, Inc.

            - Prier Products, Inc.

            - <Insert manufacturer's name>.

          - Standard: ASME A112.21.3M for [concealed] [exposed]-outlet, self-draining wall hydrants.

          - Pressure Rating: 125 psig (860 kPa).

          - Operation: Loose key.

          - Inlet: NPS 3/4 or NPS 1 (DN 20 or DN 25).

          - Outlet:

            - Concealed, with integral vacuum breaker or nonremovable hose-connection vacuum breaker complying with ASSE 1011 or backflow preventer complying with ASSE 1052.

            - Garden-hose thread complying with ASME B1.20.7.

          - Box: Deep, flush mounted with cover.

          - Box and Cover Finish: [Polished nickel bronze] [Chrome plated] <Insert finish>.

Retain "Outlet," "Box," and "Box and Cover Finish" subparagraphs above for concealed-outlet-type wall hydrants or "Outlet" and "Nozzle and Wall-Plate Finish" subparagraphs below for exposed-outlet-type wall hydrants.

          - Outlet:

            - Concealed, with integral vacuum breaker or nonremovable hose-connection vacuum breaker complying with ASSE 1011 or backflow preventer complying with ASSE 1052.

            - Garden-hose thread complying with ASME B1.20.7.

          - Nozzle and Wall-Plate Finish: [Polished nickel bronze] [Rough bronze] <Insert finish>.

          - Operating Key(s): [One] [Two] with each wall hydrant.

Copy "Vacuum Breaker Wall Hydrants" Paragraph below and re-edit for each type of wall hydrant required. If only one type is required, drawing designation may be omitted.

        - Vacuum Breaker Wall Hydrants <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - A.Y. McDonald Mfg. Co.

            - Arrowhead Brass Products.

            - Jay R. Smith Mfg. Co.

            - Mansfield Plumbing Products LLC.

            - Prier Products, Inc.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1019, Type A or Type B.

          - Type: Freeze-resistant, automatic draining with integral air-inlet valve.

Retain only Type B in "Classification" Subparagraph below if hose remains attached.

          - Classification: [Type A, for automatic draining with hose removed or ]Type B, for automatic draining with hose removed or with hose attached and nozzle closed.

          - Pressure Rating: 125 psig (860 kPa).

          - Operation: [Loose key] [or] [wheel handle].

          - Casing and Operating Rod: Of length required to match wall thickness. Include wall clamp.

          - Inlet: NPS 1/2 or NPS 3/4 (DN 15 or DN 20).

          - Outlet: Exposed with garden-hose thread complying with ASME B1.20.7.

      - GROUND HYDRANTS

Retain this article only if ground hydrants are required and are not specified in Section 221113 "Facility Water Distribution Piping." Vacuum breakers are ineffective on this type of hydrant. If using ground hydrants, a backflow preventer in supply piping is recommended.

Copy "Nonfreeze Ground Hydrants" Paragraph below and re-edit for each type of ground hydrant required. If only one type is required, drawing designation may be omitted.

        - Nonfreeze Ground Hydrants <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Jay R. Smith Mfg. Co.

            - Josam Company.

            - MIFAB, Inc.

            - Murdock-Super Secur; a member of Morris Group International.

            - Prier Products, Inc.

            - <Insert manufacturer's name>.

          - Standard: ASME A112.21.3M.

          - Type: Nonfreeze, concealed-outlet ground hydrant with box.

          - Operation: Loose key.

          - Casing and Operating Rod: Of at least length required for burial of valve below frost line.

          - Inlet: NPS 3/4 (DN 20).

          - Outlet: Garden-hose thread complying with ASME B1.20.7.

          - Drain: Designed with hole to drain into ground when shut off.

          - Box: [Standard] [Deep] pattern with cover.

          - Box and Cover Finish: [Rough] [Polished nickel] <Insert finish> bronze.

          - Operating Key(s): [One] [Two] with each ground hydrant.

Vacuum breaker in "Vacuum Breaker" Subparagraph below is ineffectual because of ground-level location. If required, include a deep box.

          - Vacuum Breaker: ASSE 1011.

      - POST HYDRANTS

Retain this article only if post hydrants are required and are not specified in Section 221113 "Facility Water Distribution Piping."

Copy "Nonfreeze, Draining-Type Post Hydrants" Paragraph below and re-edit for each type of post hydrant required. If only one type is required, drawing designation may be omitted.

Hydrants in first paragraph below are not recommended. Nonfreeze, nondraining-type post hydrants or freeze-resistant sanitary yard hydrants are preferred.

        - Nonfreeze, Draining-Type Post Hydrants <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Jay R. Smith Mfg. Co.

            - MIFAB, Inc.

            - Prier Products, Inc.

            - <Insert manufacturer's name>.

          - Standard: ASME A112.21.3M.

          - Type: Nonfreeze, exposed-outlet post hydrant.

          - Operation: Loose key.

          - Casing and Operating Rod: Of at least length required for burial of valve below frost line.

          - Casing: Bronze with casing guard.

          - Inlet: NPS 3/4 (DN 20).

          - Outlet: Garden-hose thread complying with ASME B1.20.7.

          - Drain: Designed with hole to drain into ground when shut off.

          - Vacuum Breaker:

            - Nonremovable, drainable, hose-connection vacuum breaker complying with ASSE 1011 or backflow preventer complying with ASSE 1052.

            - Garden-hose thread complying with ASME B1.20.7 on outlet.

          - Operating Key(s): [One] [Two] with each loose-key-operation wall hydrant.

Copy "Nonfreeze, Nondraining-Type Post Hydrants" Paragraph below and re-edit for each type of post hydrant required. If only one type is required, drawing designation may be omitted.

        - Nonfreeze, Nondraining-Type Post Hydrants <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by the following:

            - Murdock-Super Secur; a member of Morris Group International.

          - Operation: Lever-piston operating mechanism and nondraining water-storage reservoir, designed without drain.

          - Length: As required for burial of valve below frost line.

          - Inlet: NPS 1 (DN 25) threaded.

          - Outlet:

Retain one of first four subparagraphs below.

            - NPS 1 (DN 25) outlet and coupling plug for 1-inch (25-mm) hose.

            - NPS 1 by NPS 3/4 (DN 25 by DN 20) adapter with nonremovable, drainable, hose-connection vacuum breaker complying with ASSE 1011.

            - Garden-hose thread complying with ASME B1.20.7 on outlet.

            - NPS 1 by NPS 3/4 (DN 25 by DN 20) adapter with nonremovable, drainable, hose-connection backflow preventer complying with ASSE 1052.

            - Garden-hose thread complying with ASME B1.20.7 on outlet.

Copy "Freeze-Resistant Sanitary Yard Hydrants" Paragraph below and re-edit for each type of sanitary yard hydrant required. If only one type is required, drawing designation may be omitted.

        - Freeze-Resistant Sanitary Yard Hydrants <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by the following:

            - Hoeptner Products.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1057, Type 5 for nondraining hydrants.

          - Operation: Wheel handle.

          - Head: Copper alloy, with pail hook.

          - Inlet: NPS 3/4-inch (DN 20) threaded inlet and inlet nozzle, galvanized-steel riser, and venturi.

          - Canister: [Plastic] [Zinc-plated steel] with atmospheric-vent device.

          - Vacuum Breaker:

            - Removable hose-connection backflow preventer complying with ASSE 1052.

            - Garden-hose thread complying with ASME B1.20.7 on outlet for field installation.

      - DRAIN VALVES

Copy "Ball-Valve-Type, Hose-End Drain Valves" Paragraph below and re-edit for each type of drain valve required. If only one type is required, drawing designation may be omitted.

        - Ball-Valve-Type, Hose-End Drain Valves <Insert drawing designation if any>:

          - Standard: MSS SP-110 for standard-port, two-piece ball valves.

          - Pressure Rating: 400-psig (2760-kPa) minimum CWP.

          - Size: NPS 3/4 (DN 20).

          - Body: Copper alloy.

          - Ball: Chrome-plated brass.

          - Seats and Seals: Replaceable.

          - Handle: Vinyl-covered steel.

          - Inlet: Threaded or solder joint.

          - Outlet: Threaded, short nipple with garden-hose thread complying with ASME B1.20.7 and cap with brass chain.

Copy "Gate-Valve-Type, Hose-End Drain Valves" Paragraph below and re-edit for each type of drain valve required. If only one type is required, drawing designation may be omitted.

        - Gate-Valve-Type, Hose-End Drain Valves <Insert drawing designation if any>:

          - Standard: MSS SP-80 for gate valves.

          - Pressure Rating: Class 125.

          - Size: NPS 3/4 (DN 20).

          - Body: ASTM B 62 bronze.

          - Inlet: NPS 3/4 (DN 20) threaded or solder joint.

          - Outlet: Garden-hose thread complying with ASME B1.20.7 and cap with brass chain.

Copy "Stop-and-Waste Drain Valves" Paragraph below and re-edit for each type of drain valve required. If only one type is required, drawing designation may be omitted.

        - Stop-and-Waste Drain Valves <Insert drawing designation if any>:

          - Standard: MSS SP-110 for ball valves or MSS SP-80 for gate valves.

          - Pressure Rating: 200-psig (1380-kPa) minimum CWP or Class 125.

          - Size: NPS 3/4 (DN 20).

          - Body: Copper alloy or ASTM B 62 bronze.

          - Drain: NPS 1/8 (DN 6) side outlet with cap.

      - WATER-HAMMER ARRESTERS

Copy "Water-Hammer Arresters" Paragraph below and re-edit for each type of water-hammer arrester required. If only one type is required, drawing designation may be omitted.

        - Water-Hammer Arresters, <Insert drawing designation if any>:

For product information on Oatey’s "Quiet Pipes® Hammer Arrestors" see https://www.oatey.com/ASSETS/DOCUMENTS.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Oatey; Quiet Pipes® Hammer Arrestors, or comparable product by one of the following:

            - AMTROL, Inc.

            - Jay R. Smith Mfg. Co.

            - Josam Company.

            - MIFAB, Inc.

            - Precision Plumbing Products.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1010 or PDI-WH 201.

          - Type: Copper tube with piston.

          - Size: ASSE 1010, Sizes AA and A through F, or PDI-WH 201, Sizes A through F.

          - Fitting Size: [1/2 inch (13 mm)] [3/4 inch (19 mm)] [and] [1 inch (25.4 mm)].

          - Fitting Type: [F1960 PEX] [F1807 PEX] [MIP Thread] [Male Sweat] [Female Sweat]

          - Temperature Range: 33 to 180 deg F (0.6 to 82 deg C).

      - AIR VENTS

Copy "Bolted-Construction Automatic Air Vents" Paragraph below and re-edit for each type of air vent required. If only one type is required, drawing designation may be omitted.

        - Bolted-Construction Automatic Air Vents <Insert drawing designation if any>:

          - Body: Bronze.

          - Pressure Rating and Temperature: 125-psig (860-kPa) minimum pressure rating at 140 deg F (60 deg C).

          - Float: Replaceable, corrosion-resistant metal.

          - Mechanism and Seat: Stainless steel.

          - Size: [NPS 3/8 (DN 10)] [NPS 1/2 (DN 15)] minimum inlet.

          - Inlet and Vent Outlet End Connections: Threaded.

Copy "Welded-Construction Automatic Air Vents" Paragraph below and re-edit for each type of air vent required. If only one type is required, drawing designation may be omitted.

        - Welded-Construction Automatic Air Vents <Insert drawing designation if any>:

          - Body: Stainless steel.

          - Pressure Rating: 150-psig (1035-kPa) minimum pressure rating.

          - Float: Replaceable, corrosion-resistant metal.

          - Mechanism and Seat: Stainless steel.

          - Size: NPS 3/8 (DN 10) minimum inlet.

          - Inlet and Vent Outlet End Connections: Threaded.

      - TRAP-SEAL PRIMER DEVICE

Copy "Supply-Type, Trap-Seal Primer Device" Paragraph below and re-edit for each type of primer valve required. If only one type is required, drawing designation may be omitted.

        - Supply-Type, Trap-Seal Primer Device <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Jay R. Smith Mfg. Co.

            - MIFAB, Inc.

            - Precision Plumbing Products.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1018.

          - Pressure Rating: 125 psig (860 kPa) minimum.

          - Body: Bronze.

          - Inlet and Outlet Connections: NPS 1/2 (DN 15) threaded, union, or solder joint.

          - Gravity Drain Outlet Connection: NPS 1/2 (DN 15) threaded or solder joint.

          - Finish: Chrome plated, or rough bronze for units used with pipe or tube that is not chrome finished.

Copy "Drainage-Type, Trap-Seal Primer Device" Paragraph below and re-edit for each type of primer valve required. If only one type is required, drawing designation may be omitted.

        - Drainage-Type, Trap-Seal Primer Device <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by the following:

            - Jay R. Smith Mfg. Co.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1044, lavatory P-trap with NPS 3/8 (DN 10) minimum, trap makeup connection.

          - Size: NPS 1-1/4 (DN 32) minimum.

          - Material: Chrome-plated, cast brass.

      - TRAP-SEAL PRIMER SYSTEMS

Copy "Trap-Seal Primer Systems" Paragraph below and re-edit for each type of primer system required. If only one type is required, drawing designation may be omitted.

        - Trap-Seal Primer Systems <Insert drawing designation if any>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by the following:

            - Precision Plumbing Products.

            - <Insert manufacturer's name>.

          - Standard: ASSE 1044.

          - Piping: NPS 3/4, ASTM B 88, Type L (DN 20, ASTM B 88M, Type B); copper, water tubing.

          - Cabinet: [Recessed] [Surface]-mounted steel box with stainless-steel cover.

          - Electric Controls: 24-hour timer, solenoid valve, and manual switch for 120-V ac power.

            - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

          - Vacuum Breaker: ASSE 1001.

          - Number Outlets: [Four] [Six] [Eight] <Insert number>.

          - Size Outlets: [NPS 1/2 (DN 15)] [NPS 5/8 (DN 18)].

      - FLEXIBLE CONNECTORS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

          - Flex Pression Ltd.

          - Flex-Hose Co., Inc.

          - Flexicraft Industries.

          - Flex-Weld, Inc.

          - Hyspan Precision Products, Inc.

          - Mercer Gasket & Shim, Inc.

          - Metraflex Company (The).

          - <Insert manufacturer's name>.

        - Bronze-Hose Flexible Connectors: Corrugated-bronze tubing with bronze wire-braid covering and ends brazed to inner tubing.

          - Working-Pressure Rating: Minimum [200 psig (1380 kPa)] [250 psig (1725 kPa)].

          - End Connections NPS 2 (DN 50) and Smaller: Threaded copper pipe or plain-end copper tube.

          - End Connections NPS 2-1/2 (DN 65) and Larger: Flanged copper alloy.

        - Stainless-Steel-Hose Flexible Connectors: Corrugated-stainless-steel tubing with stainless-steel wire-braid covering and ends welded to inner tubing.

          - Working-Pressure Rating: Minimum [200 psig (1380 kPa)] [250 psig (1725 kPa)].

          - End Connections NPS 2 (DN 50) and Smaller: Threaded steel-pipe nipple.

          - End Connections NPS 2-1/2 (DN 65) and Larger: Flanged steel nipple.

      - WATER METERS

Sustainable design systems have provisions for water meters to measure fixture use separate from irrigation.

Retain this article if Contractor is to furnish water meters, and water meters are to be installed inside the building. Verify type of water meter required by the utility company and authorities having jurisdiction.

Retain "Displacement-Type Water Meters" Paragraph below for water meters NPS 2 (DN 50) and smaller. Displacement-type meters with plastic cases that comply with AWWA C710 are also available.

        - Displacement-Type Water Meters:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - AALIANT.

            - ABB.

            - Carlon Meter.

            - Mueller Co.

            - <Insert manufacturer's name>.

          - Standard: AWWA C700.

          - Pressure Rating: 150-psig (1035-kPa) working pressure.

          - Body Design: Nutating disc; totalization meter.

          - Registration: In gallons (liters) or cubic feet (cubic meters) as required by utility company.

          - Case: Bronze.

          - End Connections: Threaded.

Retain "Turbine-Type Water Meters" Paragraph below for water meters NPS 1-1/2 to NPS 10 (DN 40 to DN 250).

        - Turbine-Type Water Meters:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - AALIANT.

            - ABB.

            - Badger Industries, Inc.

            - Hays Fluid Controls.

            - Master Meter, Inc.

            - McCrometer, Inc.

            - Mueller Co.

            - <Insert manufacturer's name>.

          - Standard: AWWA C701.

          - Pressure Rating: [150 psig (1035 kPa)] <Insert value> working pressure.

          - Body Design: Turbine; totalization meter.

          - Registration: In gallons (liters) or cubic feet (cubic meters) as required by utility company.

          - Case: Bronze.

          - End Connections for Meters NPS 2 (DN 50) and Smaller: Threaded.

          - End Connections for Meters NPS 2-1/2 (DN 65) and Larger: Flanged.

Retain "Compound-Type Water Meters" Paragraph below for water meters NPS 3 (DN 80) and larger. NPS 2 (DN 50) meters are also available.

        - Compound-Type Water Meters:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - ABB.

            - Badger Industries, Inc.

            - Master Meter, Inc.

            - Mueller Co.

            - <Insert manufacturer's name>.

          - Standard: AWWA C702.

          - Pressure Rating: 150-psig (1035-kPa) working pressure.

          - Body Design: With integral mainline and bypass meters; totalization meter.

          - Registration: In gallons (liters) or cubic feet (cubic meters) as required by utility company.

          - Case: Bronze.

          - Pipe Connections: Flanged.

        - Remote Registration System: Encoder type complying with AWWA C707; modified with signal-transmitting assembly, low-voltage connecting wiring, and remote register assembly as required by utility company.

- EXECUTION

      - INSTALLATION

        - Backflow Preventers: Install backflow preventers in each water supply to mechanical equipment and systems and to other equipment and water systems that may be sources of contamination. Comply with authorities having jurisdiction.

          - Locate backflow preventers in same room as connected equipment or system.

          - Install drain for backflow preventers with atmospheric-vent drain connection with air-gap fitting, fixed air-gap fitting, or equivalent positive pipe separation of at least two pipe diameters in drain piping and pipe-to-floor drain. Locate air-gap device attached to or under backflow preventer. Simple air breaks are unacceptable for this application.

          - Do not install bypass piping around backflow preventers.

        - Water Regulators: Install with inlet and outlet shutoff valves[ and bypass with memory-stop balancing valve]. Install pressure gages on inlet and outlet.

        - Water Control Valves: Install with inlet and outlet shutoff valves[ and bypass with globe valve]. Install pressure gages on inlet and outlet.

        - Automatic Water Shutoff Valves: Test for signal strength before valve installation. Install automatic shutoff valve downstream from main domestic water shutoff valve and downstream from fire sprinkler system supply. Install valve controller is an accessible location with sensors in areas where water is likely to accumulate.

        - Balancing Valves: Install in locations where they can easily be adjusted.

        - Temperature-Actuated, Water Mixing Valves: Install with check stops or shutoff valves on inlets and with shutoff valve on outlet.

          - Install cabinet-type units recessed in or surface mounted on wall as specified.

        - Y-Pattern Strainers: For water, install on supply side of each [control valve] [water pressure-reducing valve] [solenoid valve] [and] [pump].

        - Outlet Boxes: Install boxes recessed in wall or surface mounted on wall. Install 2-by-4-inch (38-by-89-mm) fire-retardant-treated-wood blocking, wall reinforcement between studs. Comply with requirements for fire-retardant-treated-wood blocking in Section 061000 "Rough Carpentry."

        - Hose Stations: Install with check stops or shutoff valves on inlets and with thermometer on outlet.

          - Install cabinet-type units recessed in or surface mounted on wall as specified. Install 2-by-4-inch (38-by-89-mm) fire-retardant-treated-wood blocking, wall reinforcement between studs. Comply with requirements for fire-retardant-treated-wood blocking in Section 061000 "Rough Carpentry."

        - Ground Hydrants: Install with [1 cu. yd. (0.75 cu. m)] <Insert dimension> of crushed gravel around drain hole. Set ground hydrants with box flush with grade.

        - Nonfreeze, Draining-Type Post Hydrants: Install with [1 cu. yd. (0.75 cu. m)] <Insert dimension> of crushed gravel around drain hole. Set post hydrants in concrete paving or in [1 cu. yd. (0.03 cu. m)] <Insert dimension> of concrete block at grade.

        - Nonfreeze, Nondraining-Type Post Hydrants: Set in concrete or pavement.

        - Freeze-Resistant Sanitary Yard Hydrants: Set with riser pipe in concrete or pavement. Do not encase canister in concrete.

Water-hammer arresters in first paragraph below are best shown on water risers and details. Specifying number, size, and location here is difficult.

        - Water-Hammer Arresters: Install in water piping in accordance with PDI-WH 201.

        - Air Vents: Install vents at high points of water piping.[ Install drain piping and discharge onto floor drain.]

        - Supply-Type, Trap-Seal Primer Device: Install with outlet piping pitched down toward drain trap a minimum of 1 percent, and connect to floor-drain body, trap, or inlet fitting. Adjust valve for proper flow.

        - Drainage-Type, Trap-Seal Primer Device: Install as lavatory trap with outlet piping pitched down toward drain trap a minimum of 1 percent, and connect to floor-drain body, trap, or inlet fitting.

        - Trap-Seal Primer Systems: Install with outlet piping pitched down toward drain trap a minimum of 1 percent, and connect to floor-drain body, trap, or inlet fitting. Adjust system for proper flow.

      - CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Drawings indicate general arrangement of piping, fittings, and specialties.

        - When installing piping specialties adjacent to equipment and machines, allow space for service and maintenance.

Retain paragraph below if retaining "Trap-Seal Primer Systems" Article.

        - Comply with requirements for grounding equipment in Section 260526 "Grounding and Bonding for Electrical Systems."

      - IDENTIFICATION

        - Plastic Labels for Equipment: Install engraved plastic-laminate equipment nameplate or sign on or near each of the following:

Coordinate list below with products retained in Part 2.

          - Pressure vacuum breakers.

          - Intermediate atmospheric-vent backflow preventers.

          - Reduced-pressure-principle backflow preventers.

          - Double-check, backflow-prevention assemblies.

          - Carbonated-beverage-machine backflow preventers.

          - Dual-check-valve backflow preventers.

          - Reduced-pressure-detector, fire-protection, backflow-preventer assemblies.

          - Double-check, detector-assembly backflow preventers.

          - Water pressure-reducing valves.

          - Automatic water shutoff valves.

          - Calibrated balancing valves.

          - Primary, thermostatic, water mixing valves.

          - Manifold, thermostatic, water mixing-valve assemblies.

          - Photographic-process, thermostatic, water mixing-valve assemblies.

          - Primary water tempering valves.

          - Outlet boxes.

          - Hose stations.

          - Supply-type, trap-seal primer valves.

          - Trap-seal primer systems.

        - Distinguish among multiple units, inform operator of operational requirements, indicate safety and emergency precautions, and warn of hazards and improper operations, in addition to identifying unit. Nameplates and signs are specified in Section 220553 "Identification for Plumbing Piping and Equipment."

      - FIELD QUALITY CONTROL

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

        - Perform the following tests and inspections:

          - Test each [pressure vacuum breaker] [reduced-pressure-principle backflow preventer] [double-check, backflow-prevention assembly] [and] [double-check, detector-assembly backflow preventer] <Insert type> according to authorities having jurisdiction and the device's reference standard.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Domestic water piping specialties will be considered defective if they do not pass tests and inspections.

        - Prepare test and inspection reports.

      - ADJUSTING

        - Set field-adjustable pressure set points of water pressure-reducing valves.

        - Set field-adjustable flow set points of balancing valves.

        - Set field-adjustable temperature set points of temperature-actuated, water mixing valves.

END OF SECTION 221119